Annex 15
Commissioning Tests

REVISION HISTORY

| Revision Level | Change Summary | Elaborated by | Approved by | Date |
| --- | --- | --- | --- | --- |

- Overview

The Contractor will be responsible for the Commissioning of the System and performing the Performance Tests.

The testing phases are divided as follows

  - Commissioning Tests

Measures, checks and tests to be done prior to and including the connection of the Plant to the electrical grid.

- General Requirements

  - Operation during Testing and Commissioning

During the Commissioning and the Provisional Acceptance Test, the Plant will be operated by the Contractor until PAC, with the O&M Contractor’s staff in attendance under the direction and supervision of the Contractor.

After the issue of the Provisional Acceptance Certificate, the O&M Contractor shall operate the Plant in accordance with the O&M manuals provided by the Contractor. The Contractor shall remain responsible for the satisfactory performance of each test.

  - Procedures and Testing Equipment

The Contractor shall be responsible for providing all the necessary equipment, manpower, materials, consumables and services to meet his commitments with regard to this phase of the work.

The Contractor shall comply with all of the Distribution Network Operator (DNO from now on) safety procedures and be responsible for all coordination of installation and testing protocols including system and F9/F10 testing and commissioning. The Contractor shall liaise with the DNO and programme the DNO’s commissioning engineer in sufficient time so that the testing proceeds without delay.

All tests and such activities may be witnessed by the Owner’s agent or representative. Third parties may also witness some or all of the tests if and when required.

The Contractor shall make all necessary arrangements to obtain and record all test data as may be required while the Owner may check data as desired.

The Contractor shall be responsible to undertake the Commissioning Tests safely. The Contractor shall provide a safety briefing for all personnel on the Site who will be involved in or witnessing any Commissioning Test and shall ensure that such personnel comply with all applicable safety procedures at all times during performance of the Commissioning Tests. The Contractor shall discontinue performance of any Commissioning Tests in the event of any unsafe conditions.

  - Commissioning Plans, Procedures and Programme

The Contractor shall submit detailed commissioning and testing procedures to the Owner for all commissioning activities and Performance tests to be carried out. The procedures shall cover all required safety measures together with all necessary inspections, adjustments and tests to achieve progress through operation from no load to full load capacity

The Owner shall review the Contractor's submission and notify the Contractor in writing whether or not all test pre-requisites have been satisfied. If the Owner provides comments, then the Contractor shall revise the Test Protocol to address the Owner's comments and resubmit it for review and approval within two (2) business days thereafter.

If the Contractor fails to timely provide any of the required notices, such that the Owner or his Representatives are not able to witness the test then the Contractor may be required to repeat the tests at his own cost.

The testing plans shall be divided into sections for each item of Plant or system and shall include:

    - Documentation identifying the major components with references to the relevant instrumentation and interlocks.

    - A description in the form of a list, table or similar or the design operating conditions with details of all restrictions, precautions and limits on Plant operation applicable to that section of the Plant during the pre-commissioning and commissioning periods and then to subsequent operation.

    - A detailed program, for the activities to be carried out for the completion of its commissioning and performance trials.

  - Copies of the Contractor's check sheets for the pre-commissioning, commissioning and testing of each Plant item or system. Test Records

    - The Contractor shall be responsible for supplying to the Owner copies of all test documentation for the complete Plant. All original and signed test records sheets shall become the property of the Owner and shall be handed to the Owner following each test.

    - Unless noted otherwise, the Contractor shall promptly prepare and submit a detailed test report to the Owner within 15 business days of completion of any test. The test report shall include the test procedure, description of any deviations from the test procedure of unusual event(s), which occurred during the test, copies of test data sheets, calculated results, copies of lab analyses, copies of instrument calibration records, technician name and supervisor.

    - Test results should be recorded and submitted to the owner, the forms should always provide a means for recording:

      - The equipment under test and expected results

      - Test equipment used and calibration certificates.

      - The name of the person(s) who performed the test & date/time the test was carried out

      - Details of the operational testing carried out, the results of the tests and of any adjustments necessary to enable the equipment to meet its specified requirements.

      - Confirmation of pass/fail or any remedial action

      - Relevant standards (e.g. IEC 61724, Photovoltaic systems performance monitoring - Guidelines for measurement, data exchange and analysis)

    - The Contractor shall certify to the Owner in writing that the Test results and supporting data provided by the Contractor are complete, current and accurate.

    - The Owner shall confirm his acceptance or rejection of the test reports within five (5) business days of receipt.

    - If the Test results are rejected or incomplete, the Owner shall provide the basis for rejection and/or identify the missing information together with the necessary corrective action (which may include a repetition of the test).

  - In case of Dispute

    - If the Contractor disputes the Owner's rejection of any Test results or other Owner determinations with regard to the Tests Protocol, Contractor shall follow the procedure for Determinations under the Contract and if no agreement is reached the Disputes Resolution procedures set forth in the Contract.

- Commissioning Tests

The Commissioning Tests are designed to verify that the Plant is completed, connected and energised to the grid (with the F9 and F10 witness test certificate issued by the local DNO). The test sequence shall follow a structured programme with logical progression for each sub-system and system until the Commissioning is completed. The tests shall be in accordance with IEC 62446-1:2016 - Category 1 Test Regime.

The Contractor shall undertake all installation checks, preliminary mechanical and electrical checks, proving the integrity of all connections (mechanical and electrical), safety systems and verification that all Plant is functionally complete.

Once the component or system is charged, energized or otherwise made live, the Contractor shall conduct further tests to demonstrate that the system and its constituent components function collectively as designed, that individual components operate at varying loads under steady state conditions within their stated operating parameters, and that the components and system respond correctly to transient conditions. The Contractor shall undertake whatever adjustments are necessary to achieve the optimal level of Plant reliability, capacity and performance. Base line operational temperature, voltage, current, ambient data shall be recorded for all equipment and systems.

  - System documentation requirements

Prior to the start of Commissioning Tests, the Contractor shall ensure that the Owner has been provided with the latest version of all relevant documents and drawings as detailed in Annex 9.

  - Visual Inspection

All the Project components shall be visually inspected, properly documented and included as part of each Test. As a minimum, the following shall be subject to visual inspection.

- Inverters

- Foundations

- Tracking structures

- PV Modules and DC installation

- Mains, pits, cabling, electrical boxes and protection devices

- Internal connections and interconnections with external installations

- Monitoring system including any uninterruptible power supply

- Low voltage installation, including protection equipment and utility interconnection equipment

- High voltage installation, including transformation, protections equipment and utility interconnection equipment

- Security system

- Equipment labelling in agreement with plans

- Health and safety signage.

For each component, it shall be verified:

That is free of visible damage that might compromise the safety of the component and personnel

That it has been installed correctly

That the materials used and the installation techniques are appropriate to the environment in which the component is installed

That is easily accessible for the O&M Contract related activities

That the electrical installation has been carried out in accordance with the executive project and the contractual obligations defined in the Contract

The availability of the electrical drawings, safety manuals and user manuals. The identification and correct labelling of fuses, switches, circuits, etc.

The correct labelling of cables and electrical panels

The correct execution of the connections

That the component has been installed according to the manufacturer’s guidelines

The existence of the necessary protections against electric shocks due to indirect contact

The serial/ID numbers of the modules have been mapped unto and associated with their respective flash test data, trackers and inverters (“module mapping”).

The existence of reports on factory tests or reports on the manufacturer's quality tests, if applicable

The Contractor certifies in writing that the work has been carried out in compliance with the applicable laws

Additionally, with the visual inspection it shall be verified that the installation of all the components is in line with the as-built design with a focus on the following items:

Labelling

Nominal capacity of the components

Distances, heights, and position of the components

Cable and busbar sizes

PV Modules flash tests

Torque marks

  - DC Circuits (Module Strings)

Commissioning Tests shall will be carried out in accordance with IEC 62446 (Category 1 Test Regime).

All low voltage DC and AC cables must be tested for insulation resistance according to IEC 60364-6, IEC 60364-7 and other applicable standards

All low-voltage cables must be inspected and tested in accordance with IEC 60364-6, IEC 60364-7 and other applicable standards.

The following referenced documents are indispensable for the application of this standard.

For dated references, only the edition cited applies. For undated references, the latest edition of the referenced document (including any amendments) applies.

    - IEC 60364 (all parts, to the extent to which they may be applicable), Low-voltage electrical installations

    - IEC/TR 60755:2008, General requirements for residual current operated protective devices.

    - IEC 61557 (all parts), Electrical safety in low voltage distribution systems up to 1000 V AC and 1500 V DC – equipment for testing, measuring or monitoring of protective measures

    - IEC 62446, Minimum requirements for system documentation, commissioning tests

These tests are to verify that the strings have been correctly configured prior to connection to the electrical network and should be carried out when the irradiation is greater than 500W/m².

All measurements must be carried out using suitably rated & calibrated measurement devices, including I-V curve diagnostic tools, which have a measurement accuracy of ±1% or better. If a string monitoring device with acceptable precision and tolerance levels as indicated above is used, such as the case of an inverter with I-V diagnostics tools (such as Huawei Smart IV Curve diagnosis), the cell temperature and irradiance values measured using the site’s meteorological stations can be considered to perform this analysis, although 5% of the strings will be measured with independent calibrated measurement devices in order to validate inverter IV diagnosis.

All personnel must wear the correct PPE and be trained in the safety aspects of performing these tests.

    - Open Circuit Voltage Check

Calculate and record the expected string open circuit voltage using the following formula Vocs = N · Voc (1 + TC · (T - 25))

Where

| Vocs | is the expected string open circuit voltage |
| --- | --- |
| N | relates to the number of modules in the string |
| Voc | is the module open circuit voltage at stc.* |
| TC | is the Temperature Coefficient of Open Circuit Voltage* |
| T | is the temperature recorded on the photovoltaic module representing the tested string, measured with an infrared thermometer with a precision better than ± 1%; |

* taken from module datasheet

The test shall measure and record the actual open circuit voltage (Vactual) of all PV strings in the Solar Park. This can be done without disconnecting cables by making the measurements in the string boxes.

Before taking voltage measurements in each string box measure and record the irradiance in the array plane.

With all string fuses open, measure and record the voltages across the positive and negative terminals in the string boxes for 100% of strings in the Solar Park.

For test periods where the irradiance conditions are stable, then compare the voltages between strings and verify that these all have the same polarity and are all within ±5% of the average value (per inverter) and are all within ±10% of the calculated value.

For non-stable irradiance conditions, then a correction factor will need to be applied

    - Short Circuit Current check

The string box is arranged to measure two strings in parallel, but the short circuit current check will be done in each single string (or Y-string) separately.

Prior to commencement of the short circuit test, measure and record the irradiance in the array plane.

The short circuit current shall satisfy the following conditions:

95% of ISC_Expected ≤ ISC

ISC_Expected = ISC_ref * GMeasured / GSTC

| ISC_Expected | It is the theoretical short circuit current of the string |
| --- | --- |
| ISC_ref | It is the short circuit current of the string as indicated on the module’s datasheet |
| GMeasured | It is the irradiance measured at the same tilt and the same azimuth of the modules. The irradiance shall be measured with a pyranometer with an accuracy higher than ± 1%. In case that an I-V tracer is used, its irradiance sensor can be used. |
| GSTC | It is the irradiance at standard conditions, 1,000W/m2 |

With all inputs isolated from each other and all disconnecting means in their open position, introduce a temporary short circuit across the strings under test using a purpose designed and suitably rated “short circuit switch test box”, measure and record the s/c current.

All voltage and current measurements must be carried out using suitably rated & calibrated measurement devices, including I-V curve diagnostic tools, which have a measurement accuracy of ±1% or better. If a string monitoring device with acceptable precision and tolerance levels as indicated above is used, such as the case of an inverter with I-V diagnostics tools (such as Huawei Smart IV Curve diagnosis), the cell temperature and irradiance values measured using the site’s meteorological stations can be considered to perform this analysis, although 5% of the strings will be measured with independent calibrated measurement devices in order to validate inverter IV diagnosis.

    - Insulation Resistance (Strings to DC Combiner Boxes / String Inverters)

ALWAYS OBSERVE THE OPERATING INSTRUCTIONS OF THE TEST EQUIPMENT PROVIDER

TEST METHOD 1 – Whilst the string is not connected in short circuit, connect a Megger or other suitable device to the system to enable the application of a test voltage of 1500V between the string pole (alternate between positive and negative) and ground. Alternatively, a specific device that measure Voc, Isc and cable isolation, all 3 measures at once, can be used instead of a Megger.

TEST METHOD 2 – Whilst the string is still connected in short circuit, connect a Megger or other suitable device to the system to enable the application of a test voltage of 1500V between the short circuited array string and ground. Alternatively, a specific device that measure Voc, Isc and cable isolation, all 3 measures at once, can be used instead of a Meger.

Record the resulting insolation resistance and verify that this is greater than 1MΩ. Disconnect the Megger from the circuit and remove the short circuit from array string.

    - Insulation Resistance (DC Combiner Boxes to Power Stations)

ALWAYS OBSERVE THE OPERATING INSTRUCTIONS OF THE TEST EQUIPMENT PROVIDER

TEST METHOD 1 – Whilst the array is not connected in short circuit, connect a Megger or other suitable device to the system to enable the application of a test voltage of 1500V between the array pole (alternate between positive and negative) and ground.

TEST METHOD 2 – Whilst the array is still connected in short circuit, connect a Megger or other suitable device to the system to enable the application of a test voltage of 1500V between the short circuited array and ground.

Record the resulting insolation resistance and verify that this is greater than 1MΩ.

Disconnect the Megger from the circuit and remove the short circuit from Combiner boxes to Power Stations.

    - I-V curves

The I-V curves will be carried out in 100% of the strings, with a minimum radiation of 500 W / m2, utilizing the string inverter I-V diagnostic function (such as Huawei Smart IV Curve diagnosis). Systems connected to the network. Documentation, start-up and inspection tests.

  - MV Cables

Once the MV circuit has been completed (all connections to transformers and protection devices completed) then pressure tests must be performed on all MV cables by a specialist contractor in accordance with an approved method statement.

  - Earthing

Perform a site earthing test to verify that the earth resistance is less than that given in the earthing report.

  - Grid, Inverters & MV Circuits

The procedures and timing for these tests will be subject to the agreement of the Grid operator. The test sequence will be established in conjunction with the DNO and may differ from the normal requirements noted herein

  - Thermographic inspection

Thermographic inspection shall be performed on 100% of the PV Modules. The purpose of the thermographic inspection is to identify any anomalous temperature variations in the PV Modules.

The irradiance in the plane of the array must be greater than 600 W/m2 with stable climatic conditions. Ideally, the irradiance in the plane of the array should be relatively constant and more than 700 W/m2 to ensure that there is enough current to cause distinguishable temperature differences. The plant will be therefore energized.

Each module in the array or sub-array in question will have to be analysed paying particular attention to block diodes, junction boxes, electrical connections or any other part of the array that shows a significant temperature difference.

When scanning from the front of an array, the camera and operator should not project shadows onto the area under examination. A drone might be used for checking PV Modules, in case the Owner previously approves it. In case that manual thermographic camera is used, all PV Modules would be checked, taking pictures in those PV Modules with defects.

The analysis must be performed by certified personnel and in accordance with the reference technical standards for thermography. Uncertified personnel could also carry out the analysis, but previous approval by the Owner is needed Thermographic inspection will be carried out once the plant is energized.

  - SCADA

The commissioning of the SCADA system has the purpose of verifying the correct functioning of the system itself and of all the components monitored by it, verifying in particular:

•	The proper recording of data from all the components monitored by the system

•	That the data can be used to produce any report on the performance or operation required

•	That each line of data reports the exact date and time in an appropriate format

•	That the SCADA system is completely accessible from the remote.

•	Proper functioning of the UPS

•	Remote control to recloser and inverters.

•	Tracking system parameters and status gain (compare horizontal irradiance with tracker irradiance).

•	Firewall System.

  - Isolation monitoring system

The Contractor shall check that all the isolation monitoring system from Inverters and Power Station supplier work properly together. The Contractor shall check this aspect for the whole plant.

  - Security system

The commissioning of the security system includes the verification of all operating modes and alarm conditions, including the verification of:

Cameras and dome cameras

Image analyser

Infrared sensors

Infrared barriers, microphone cables, microwave barriers (if any)

Lights

Sirens

Response time of the security company.

UPS performance. Duration.

Final verifications shall depend on the installed security system.

    - Cold Commissioning (F9)

Commissioning of DNO and Customer switchgear protection will be carried out, together with the DNO, to verify correct switching operations through the simulation of grid problems and verification of the protocols prior to connecting the plant to the electrical grid.

    - Provisional Electrical Connection (F10)

After completion of the cold commissioning and installation of the export meter a provisional electrical connection will be agreed with the DNO to allow testing of the inverters prior to final F10 loss of mains test according DNO procedure.

    - Inverters

The inverter manufacturer or a contractor certified by the inverter manufacturer will configure and commission the inverters in accordance with the manufacturer’s test protocols and certify that the equipment is correctly connected and working properly.

    - F10 Witness Test

Once all inverters have been tested and certified to be fully operational the Owner will call the DNO to perform the final, loss of mains, F10 witness testing.